NOTE: Effective January 1, 2023,

National Grid will require all inverter-based systems to meet IEEE 1547-2018 and UL 1741 SB certification.  All inverter-based interconnection applications received on or after January 1, 2023, must show proof of compliance with these standards and settings in order to be considered a completed application.

### Utility Grade Relay and UL 1741 SB Certified Inverter Parallel Generation Default Voltage & Frequency Set points

| DEVICE | PICKUP RANGE (Defaults set points in bold) | DEFAULT CLEARING TIME (sec) |
| --- | --- | --- |
| Under Frequency (81U) | < 56.5 Hz | 0.16 |
| Under Frequency (81U) | < 58.5 Hz | 300 |
| Over Frequency (81O) | 61.2 Hz < f <62.0Hz | 300 |
| Over Frequency (81O) | > 62.0 Hz | 0.16 |
| Under Voltage (27) | < 50% of Nominal | 1.1 |
| Under Voltage (27) | 50% <V< 88% of Nominal | 3 |
| Over Voltage (59) | 110% <V< 120% of Nominal | 2 |
| Over Voltage (59) | ≥ 120% of Nominal | 0.16 |

Settings other than the default, within the settings ranges in IEEE 1547, may be acceptable on a case-by-case basis and are subject to review and approval by the Company. DER facilities with Direct Transfer Trip installed may be required to have wider than the default settings to comply with ride through requirements.

Note that consistent with IEEE 1547, the pickups are exact set points, and the time delays are maximum total clearing times (including relay and device interruption time).

### Default Volt-VAR Settings for Inverter-based Utility Interactive DER

| Required Parameter | Default Settings Setpoint |
| --- | --- |
| Vref | Vn |
| V1 | 0.93 per unit of nominal voltage |
| Q1 | 44% of Inverter Reactive Capacity |
| V2 | 0.97 per unit of nominal voltage |
| Q2 | 0% of Inverter Reactive Capacity |
| V3 | 1.03 per unit of nominal voltage |
| Q3 | 0% of Inverter Reactive Capacity |
| V4 | 1.07 per unit of nominal voltage |
| Q4 | -44% of Inverter Reactive Capacity |
| Open Loop Response Time | 5s |
| Autonomous Vref enablement | OFF |

Settings other than the default, within the ranges in IEEE 1547, may be acceptable on a case-by-case basis and are subject to review and approval by the Company.

### Default Volt-Watt Settings for Inverter-based Utility Interactive DER

| Required Parameter | Default Settings Setpoint |
| --- | --- |
| V1 | 1.07 per unit of nominal voltage |
| P1 | Prated |
| V2 | 1.10 per unit of nominal voltage |
| P2 | The lesser of 0.2 Prated or Pmin |
| P”2 (absorption, storage only) | 0 |
| Open Loop Response Time | 10s |

Unless otherwise specified by the Company, Volt-WATT shall be disabled by default. Otherwise, the default settings for Volt-WATT are required to have setting ranges according to the following table above. Settings other than the default, within the ranges in IEEE 1547, may be acceptable on a case-by-case basis and are subject to review and approval by the Company.

### Default Frequency-Watt Settings for DER UL1741SB Certified Inverters

| Required Default Settings |  | Comparison to IEEE Std. 1547-2018 Default Settings for Category III |  |
| --- | --- | --- | --- |
| Parameter | Settings | Settings | Within ranges of allowable settings? |
| dbOF, dbUF (Hz) | 0.036 | Identical | Yes |
| kOF, kUF | 0.05 | Identical | Yes |
| T-response (small-signal) (s) | 5 | Identical | Yes |

### Return to Service Parameters for DER

| Utility Voltage Parameter | Default Value |
| --- | --- |
| Minimum Return to Service Voltage: | 0.95 per unit of nominal voltage |
| Maximum Return to Service Voltage: | 1.05 per unit of nominal voltage |
| Minimum Return to Service Frequency: | 59.5 Hz |
| Maximum Return to Service Frequency: | 60.5 Hz |
| Default return to service Ramp time (Enter Service Period) | 300s |

For DER less than 50 kW, Voltage Reactive Power Mode (Volt/Var) set to OFF