## DG Action Item List (hidden)
Project: | Enter Project Name
Case # | Enter Case #
From: | Enter DG /Protection Engineer (National Grid)
To: | Enter Customer Name
Category | Requirement | Status | Date Closed | Date Submitted | Salesforce Form # | Sheet Number | Source of Requirement | National Grid Comments Enter Comments | Customer Response Enter Date
General | All Customer poles and interconnection devices, including switches, breakers, fuses, busses and transformers shall be uniformly placarded with permanently affixed metal or plastic labels. |  |  | Enter Date of submission | Enter Salesforce Form # | Enter Sheet Number if Applicable | Stated in ESB 751 Section 5.0 [edited].
General | The main generator disconnect switch shall be capable of being locked in the open position and have provisions for both Company and Generator-Owner or IC padlocks. | [5 empty] | State in ESB 756 Section 5.1 [edited].
General | Should the disconnecting means be located behind the IC's locked gate, double locking is required, where both the Company's and IC's locks would be employed. | [5 empty] | Stated in ESB 756 7.4.5.
General | The utility meter enclosure shall be labeled with the following: "WARNING: DUAL POWER SOURCES" | [5 empty] | Stated in ESB 756 Section 7.2.1.
General | The final approved single-line diagram shall be laminated and located on the customer site at the GOAB in a PVC pipe. | [5 empty] | Not directly in ESBs. Mentioned in the Witness Test document.
General | The GOAB Shall have a permanent nameplaate at the switch pole indication " GOAB" or Main Generator Disconnect
Electrical AC Elementary Drawing (Three-Line Diagram) | The three-line diagram shall be PE stamped. Until approved, the diagram shall have a note or watermark stating "NOT FOR CONSTRUCTION". | Open |  |  |  |  | Stated in ESB 751 Section 5.0 for single line [edited].
Electrical AC Elementary Drawing (Three-Line Diagram) | The three-line diagram shall show the entire system through the electrical generator connection. It shall include: all protective devices including ratings and classes in sufficient detail to show intended operation; all instrument transformers with ratios; power and station service transformers with ratios, kVA, winding configurations, impedances; etc. | Open |  |  |  |  | Stated in ESB 751 Section 5.0 for single line.
Electrical AC Elementary Drawing (Three-Line Diagram) | Switches and/or fuses shall be shown as dead-ended on the source side of the equipment. | Open |  |  |  |  | Not directly stated in ESBs.
Electrical AC Elementary Drawing (Three-Line Diagram) | The three-line diagram shall be updated to adequately show information post-construction such as actual transformer and/or grounding transformer values, equipment nameplates, etc. at least two weeks prior to the witness test date. | Open |  |  |  |  | Not directly stated in ESBs.
Electrical AC Elementary Drawing (Three-Line Diagram) | The Company shall assign the Customer interconnection devices, including switches, breakers, fuses, device numbers which aid in communications and coordination during switching operatings between the Company and the Customer. - Main Disconnect Switch: C511 - Customer Recloser: CR512 OR - Customer Fuse: J512 - Customer Additional Disconnect Switch: C513 | Open |  |  |  |  | Stated in ESB 751 Section 5.0 [edited].
Electrical AC Elementary Drawing (Three-Line Diagram) | The Customer shall include appropriate numbering for the Customer poles. - Customer Pole Numbers: C(POI pole)-1, C(POI pole)-2, C(POI pole-3) | Open |  |  |  |  | Stated in ESB 751 Section 5.0 [edited].
Electrical AC Elementary Drawing (Three-Line Diagram) | Utility equipment shall have a note stating that the utility equipment is shown for reference purposes only, is not for construction, and may be changed by the utility at any time in the future. | Open |  |  |  |  | Not directly stated in ESBs.
Electrical AC Elementary Drawing (Three-Line Diagram) | Customer main generator disconnect shall be labeled to reflect that it is utility lockable with 24-hour/7-day access and control by the utility and that it is capable of being locked in the open position with a visible break. | Open |  |  |  |  | Not directly stated in ESBs.
Electrical AC Elementary Drawing (Three-Line Diagram) | It is recommeded that the customer install a switch capable of a visible open and a lightning arrester on the riser pole. | Open |  |  |  |  | Not directly stated in ESBs.
Electrical Single-Line Diagram | The single-line diagram shall include all equipment shown on the three-line diagram as well as all requirements. The single-line and three-line must be consistent. | Open |  |  |  |  | Reversed in ESB 751 Section 5.0 but still the same. Last sentence added for clarity.
Electrical DC Control Schematic | The electrical DC control schemetic shall show all control diagrams of the equipment associated with the interconnection protective system. Control diagrams depict all logic used to control the interconnection protective devices. Relay logic diagrams shall be provided for utility-grade relay functions meeting utility requirements (i.e. including grounding bank shunt trip or UVR schemes). | Open |  |  |  |  | Stated in ESB 756 Section 2.2.2.1.4. Last sentence is added for clarity.
Site Plan | The site plan shall be PE stamped. Until approved, the diagram shall have a note or watermark stating "NOT FOR CONSTRUCTION". | Open |  |  |  |  | Stated in ESB 751 Section 5.0 for single line [edited].
Site Plan | The site plan shall consist of the location of major customer equipment, the Company equipment to be installed on site, and site details that will be helpful to define accessibility of the site. Site plans shall be to scale with approximate distances indicated, north arrow and scale bar. | Open |  |  |  |  | Stated in ESB 756 Section 5.1.1.3.
Site Plan | The Company shall assign the Customer interconnection devices, including switches, breakers, fuses, device numbers which aid in communications and coordination during switching operatings between the Company and the Customer. - Main Disconnect Switch: C511 - Customer Recloser: CR512 OR - Customer Fuse: CJ512 - Customer Additional Disconnect Switch: C513 | Open |  |  |  |  | Stated in ESB 751 Section 5.0 [edited].
Site Plan | The Customer shall include appropriate numbering for the Customer poles. - Customer Pole Numbers: C(POI pole)-1, C(POI pole)-2, C(POI pole-3) | Open |  |  |  |  | Stated in ESB 751 Section 5.0 [edited].
Site Plan | Utility equipment shall have a note stating that the utility equipment is shown for reference purposes only, is not for construction, and may be changed by the utility at any time in the future. | Open |  |  |  |  | Not directly in ESBs.
Site Plan | Customer main generator disconnect shall be labeled to reflect that it is utility lockable with 24-hour/7-day access and control by the utility and that it is capable of being locked in the open position with a visible break. | Open
Site Plan | Access road shall have a minimum width of 20 feet and a turnaround area for vehicles to exit without backing up should be provided where possible. | Open
Profile Drawings | The profile drawings shall consist of a minimum of two perpendicular cuts of the site plan. Profiles shall be in sufficient detail to allow for the Company's determination of electrical and working space clearances. At a minimum, a single drawing of the entire line-up shall be provided. | Open |  |  |  |  | Stated in ESB 751 Section 5.0. Last sentence is added for clarity.
Profile Drawings | The Customer shall include appropriate numbering for the Customer poles. - Customer Pole Numbers: C(POI pole)-1, C(POI pole)-2, C(POI pole-3) | Open |  |  |  |  | Stated in ESB 751 Section 5.0 [edited].
Profile Drawings | The profile drawings shall show phase-to-phase and phase-to-ground clearances as well as pole-to-pole distances. | Open |  |  |  |  | Stated in ESB 753 [edited].
Profile Drawings | The Customer's overhead conductors shall have a minimum clearance of 22 feet from final grade. Minimum distnace between primary and neutral shall be 72 inches and minimum distance between bottom fo PT/CT mount shall be 20 inches | Open |  |  |  |  | Stated in ESB 753 Section 4.B.4.
Profile Drawings | Poles shall be minimum Class 5, full length penta treatment, comforming to the standards of EEI TD-103 and ANSI O5.1. | Open |  |  |  |  | Stated in ESB 753 Section 5.B.1.
Profile Drawings | Poles shall be a minimum of 40 ft. in height, set 6 ft. minimum depth. | Open |  |  |  |  | Stated in ESB 753 Section 5.B.1.
Profile Drawings | The crossarm shall measure 3-1/2" x 4-1/2" x 8'-0" minimum, comforming to specifications of EEI TD-90. A dead-end crossarm such as a riser pole must be a double-crossarm if made of wood. | Open |  |  |  |  | Stated in ESB 753 Section 5.B.2.
Profile Drawings | Guy wires shall be 25 ft. mimimum lead with insulator. - Guy wires shall utilize an insulating rod that is minimum 54" long, but longer if there is the potential to come into contact with energized equipment upon failure of the guy wire anchor. - The section of the guy wire below the insulating rod shall be bonded to neutral. - Clearance from the insulating rod to the primary conductor shall be a minimum of 6" for down guys, or 11" minimum for span guys. - Anchor shall be buried 6 ft. in ground minimum. | Open |  |  |  |  | Stated in ESB 753 Section 5.B.3 [edited].
Profile Drawings | The switch shall be mounted so that the handle will be approximately 3'-6" above grade. | Open |  |  |  |  | Stated in ESB 753 Section 5.C.2.
Profile Drawings | The main disconnect switch mechanism shall be connected to the grounding grid near the operating handle by means of a flexible, tinned copper braid of at least 200 Ampere rating. The grounding grid and the switch handle's ground strap shall be connected to the pole's grounding conductor. | Open |  |  |  |  | Stated in ESB 753 Section 6.A.
Profile Drawings | The disconnect switch shall be installed to have the line connection (i.e., jaw side) of the switch connected to the utility source. Hinge side of switch shall be connected electrically towards the customer DER. | Open |  |  |  |  | Stated in ESB 756 Section 7.4.2.
Profile Drawings | All non-current carrying metallic parts shall be bonded to equipment ground with a stranded #4 AWG bare copper conductor. This includes switch frame (unless composite), guy wires, switch base, and the neutral. | Open |  |  |  |  | Stated in ESB 753 Section 6.A.
Profile Drawings | Lightning arresters shall have a separate stranded #4 AWG bare copper conductor to the ground grid. Customer-owned reclosers with factory shipped grounding provisions will be exempt from this rule. | Open |  |  |  |  | Stated in ESB 753 Section 6.A.
Profile Drawings | At least 2 ground rods shall be used. They shall be at least 5/8" x 8'-0" with clamps. | Open |  |  |  |  | Stated in ESB 753 Section 6.A.
Profile Drawings | The ground rods shall be buried at least 6 inches below grade. | Open |  |  |  |  | Stated in ESB 753 Section 6.A.
Profile Drawings | The rods shall be spaced at a minimum distance of 3 ft. from the center of the pole, and at least 6 ft. minimum from each other. Photos of below grade grounding installation shall be submitted to National Grid for review prior to backfill. | Open |  |  |  |  | Stated in ESB 753 Section 6.A. Last sentence is added for clarity.
Profile Drawings | The ground rods shall be bonded together with #4 AWG bare copper conductor. Photos of below grade grounding installation shall be submitted to National Grid for review prior to backfill. | Open |  |  |  |  | Stated in ESB 753 Section 6.A. Last sentence is added for clarity.
Profile Drawings | A 5' x 6' grid of 8" x 8" copperweld mesh shall be installed below the operating handle of the switch, recloser cabinet and meter cluster to protect servicing personnel. It is additionally recommended that the customer installs a grounding grid below any of their additional equipment that has the potential to become energized but this is not required. | Open |  |  |  |  | Stated in ESB 753 Section 6.B. Last sentence is added for clarity.
Profile Drawings | The grid shall have 3" of #2 crushed stone beneath it and shall be laid 3 inches below grade, covered by #2 crushed stone. Photos of below grade grounding installation shall be submitted to National Grid for review prior to backfill. | Open |  |  |  |  | Stated in ESB 753 Section 6.B. Last sentence is added for clarity.
Profile Drawings | Meter shall have 1-1/2" rigid metallic or schedule 80 P.V.C. conduit installed by customer. | Open |  |  |  |  | Stated in ESB 753 Figure 4 Notes.
Profile Drawings | Equipment on poles shall adhere to distances set forth in ESB 753 Figure 4, 5 and 6. | Open |  |  |  |  | Not directly stated in ESBs.
Protective Device Information | The protective device information shall incorporate a summary list of proposed relay settings and/or fuse curve (note: Settings shall not be shown on drawings to avoid repeated PE stamping during setting review). | Open |  |  |  |  | Stated in ESB 751 Section 5.0 [edited]
Protective Device Information | Customer to provide relay setting file(s) in manufacturers native format (i.e. .rdb) | Open |  |  |  |  | Not directly stated in ESBs.
Detailed Manufacturer's Cut Sheets | Transformer Manufacturer's Approval Drawings - shall include outline drawings including winding configurations, taps, impedances, X/R ratio, etc. Submitted documentation shall highlight product numbers and information for the specific equipment/devices that will be installed as part of the project. | Open |  |  |  |  | Stated in ESB 751 Section 5.0 [edited].
Detailed Manufacturer's Cut Sheets | Transformer Manufacturer's As-Built Test Reports - shall include outline drawings including winding configurations, taps, as-built impedances, X/R ratio, etc. Submitted documentation shall highlight product numbers and information for the specific equipment/devices that will be installed as part of the project. | Open |  |  |  |  | Not directly stated in ESBs.
Detailed Manufacturer's Cut Sheets | Grounding Transformer Manufacturer's Approval Drawings - shall include nameplate, test reports and outline drawings including winding configurations, taps, impedances, X/R ratio, etc. Submitted documentation shall highlight product numbers and information for the specific equipment/devices that will be installed as part of the project. | Open |  |  |  |  | Stated in ESB 751 Section 5.0 [edited].
Detailed Manufacturer's Cut Sheets | Grounding Transformer Manufacturer's As-Built Test Reports - shall include nameplate, test reports and outline drawings including winding configurations, taps, impedances, CT test reports, etc. Submitted documentation shall highlight product numbers and information for the specific equipment/devices that will be installed as part of the project. | Open |  |  |  |  | Not directly stated in ESBs.
Detailed Manufacturer's Cut Sheets | Main Disconnect Switch Manufacturer's Cut Sheets - Submitted documentation shall highlight product numbers and information for the specific equipment/devices that will be installed as part of the project. The cut sheet shall include the following items: - Nameplate - Ratings (shall be 14.4 kV, 110 kV BIL minimum with a minimum ampacity of 400 A continuous) - Ability to operate properly with a 10,000 ft.-lb (2,000 lbs. tension per conductor) torque applied to the switch mounting frame - Capable of opening under 1/2" ice loading conditions - The proposed switch mounted - A bill of material identifying the quantity, material, size, model, and catalog number of all components associated with the switch including the switch itself, mounting frame and the operating mechanism and hardware | Open |  |  |  |  | Stated in ESB 751 Section 5.0 and ESB 756 [edited].
Detailed Manufacturer's Cut Sheets | Circuit Breaker Manufacturer's Cut Sheets - shall include BIL ratings, continuous symmetrical and asymmetrical interrupting ratings, control voltage source, CT test reports, related nameplate data, etc. Submitted documentation shall highlight product numbers and information for the specific equipment/devices that will be installed as part of the project. | Open |  |  |  |  | Stated in ESB 751 Section 5.0 and ESB 756 [edited].
Detailed Manufacturer's Cut Sheets | Circuit Breaker Tripping Energy Source Cut Sheets - shall identify type of energy source used (battery, capacitor, UPS, etc.). The source shall be shown to be adequate to trip the breaker(s) under low voltage and no voltage conditions. | Open |  |  |  |  | Stated in ESB 751 Section 5.0 and ESB 756 [edited].
Detailed Manufacturer's Cut Sheets | Fuse Manufacturer's Cut Sheets - shall include TCC curve number with minimum melt and total clear curves, symmetrical and asymmetrical interrupting ratings, and ratings of the fuse cut-outs. Submitted documentation shall highlight product numbers and information for the specific equipment/devices that will be installed as part of the project. | Open |  |  |  |  | Stated in ESB 751 Section 5.0 and ESB 756 [edited].
Detailed Manufacturer's Cut Sheets | Relay Manufacturer's full specified model number and firmware version. Relay operating manual may be required if requested by the Company. | Open |  |  |  |  | Stated in ESB 751 Section 5.0 and ESB 756.
Detailed Manufacturer's Cut Sheets | Inverter Manufacturer's Cut Sheets - shall include inverter-based system models and validation test data as well as UL 1741 Certification. Submitted documentaiton shall highlight product numbers and information for the specific equipment/devices that will be installed as part of the project. | Open |  |  |  |  | Stated in ESB 756 Section 5.1.1.2.
Detailed Manufacturer's Cut Sheets | Inverter Manufacturer's Cut Sheets - De-rating of inverter-based DER shall only be considered if the equipment is provided by the IC's manufacturer with a permanent means of reducing the rated output, and so marked with an equipment nameplate stating the de-rated output. | Open |  |  |  |  | Stated in ESB 756 Section 1.3.2.
Detailed Manufacturer's Cut Sheets | Lightning Arrester Manufacturer's Cut Sheets - Shall be rated according to ESB 753 Section 5. Submitted documentation shall highlight product numbers and information for the specific equipment/devices that will be installed as part of the project. | Open |  |  |  |  | Not directly stated in ESBs.
Customer Notifcation of Satisfactory Completion of Construction | At least two weeks prior ot the Company's field audit, the Interconnection Customer shall provide written documentation of satisfactory construction completion. This shall include the contractor's functional testing schedule and Testing and Commissioning Plan for the protective relay systems. | Open |  |  |  |  | Stated in ESB 751 Section 6.1 [edited].
Electrical Inspection by Code Enforcement Authority | The Customer shall provide evidence of an electrical inspection, performed by the Authority Having Jurisdiction or their assigned agent. The Customer's third party or minicipal electrical inspection approval certificate shall be submitted to the Company before the Company's on-site field audit of the Customer's site. | Open |  |  |  |  | Stated in ESB 751 Section 6.1.5.
Company's Field Audit | The Company shall make a final walk-through field audit of the Customer site to confirm the construction is in substantial conformance with the Company accepted design submittals. The Company will also verify final grounding attachments, observe related safety signs and fencing, and ensure the Company has access to the main disconnect device, as a condition of acceptance. During the Company's Field Audit, the Company shall verify the permanently installed placards on the specific devices, as required by the Company. The placards shall be clearly visible to operators. | Open |  |  |  |  | Stated in ESB 751 Section 6.1.4.
Customer Operating Agreement and Company Operating Diagram | National Grid requires a list of 24 hour emergency contacts from the Customer, once their facility is interconnected to the National Grid distribution system. The Customer shall provide a list of the primary and alternate contact personnel in the order in which National Grid should attempt to contact them. The Company will issue the Customer Operating Agreement and a Company Operating Diagram specific to the Customer installation, each containing the customer's emergency contacts. | Open |  |  |  |  | Stated in ESB 751 Section 6.1.6 [edited].
Maintenance Plan | The maintenance plan shall identify the specific equipment to be maintained and the maintenance schedule. See the Company's ESB 755 for guidance. | Open |  |  |  |  | Stated in ESB 751 Section 5.0.
Energization Plan | The Customer shall designate an Energization Coordinator, and prepare and submit an Energization Plan to the Company for review and comment.The Energization Plan shall include but not be limited to such items as: - Switching control procedures; - Required phasing and synchronization tests; - Load and operational tests required to place the apparatus or systems on line without risk to the electrical infrastructure; and - Sequence of Operations which explains how automated switching will occur based on planned and unplanned outage events, and the automatic restoration back to original conditions. Correct breaker, bus, transformer, and disconnect nomenclature shall be referenced throughout this procedure, and shall be consistent with the submitted three line diagram. | Open |  |  |  |  | Stated in ESB 751 Section 7.3.2.
Witness Test (Testing and Commissioning Plan) | The testing and commissioning plan shall include the procedural steps for testing and functional verification of the Customer's relay, breakers, interlocking schemes, and related protection devices. The Company has an interest in witnessing portions of the overall test specific to those devices which interconnect to the Company's EPS. The Company reserves the right to modify the testing procedure as necessary to ensure the integrity of the Company's EPS. | Open |  |  |  |  | Stated in ESB 751 Section 5.0.
As-Built Documentation | As-build documentation is required at the end of the design process. Within 120 days of energization, the Customer shall submit a full set of the drawings and documents in States B and C of ESB 751. | Open |  |  |  |  | Stated in ESB 751 Section 8.0.

## DG Action Item List Template
Project: | Enter Project Name
Case Number: | Enter Case Number
From: | Enter National Grid Interconnection Engineer and Protection Engineer
To: | Enter Customer Name
Primary Meter Configuration: | Primary Meter Pole
[7 empty] | First Review Cycle (Enter Date) |  |  | Second Review Cycle (Enter Date)
Category | Requirement Minimum requirements subject to current version of National Grid's ESBs and its Erratas with effective dates prior to Customer initial submission of Stage B documentation. | Status | Date Closed | Date Submitted | Salesforce Form Name | Salesforce Form Number | Latest Submittal Reviewed | National Grid Comments | Customer Response (Enter Date) | Latest Submittal Reviewed | National Grid Comments | Customer Response (Enter Date)
*** STORMS 172R Requirements SHALL NOT BE COMPLETED until initial site plan is ready for site visit***
Site Plan | Location and labeling of POI devices (poles and/or switchgear) General Guidance: 1. Pole locations match what was determined and discussed during the initial site visit 2. Site access road (20' wide, poles 5-10' from road edge) 3. Pole distances (25' minimum for distribution, 30' minimum for sub-transmission) 4. Switchgear locations and distances including bollarding locations. ESB 751 Section 5.0 ESB 756B Section 5.1.1.3 | Open |  |  | Site Plan
Site Plan | 1. Location and labeling of all field devices (poles, inverters, MV equipment, etc.) 2. Locations of Company Equipment shall be noted as "Utility Equipment is for information purposes only, is not for construction, and may be changed by the Utiltiy at any time in the future." 3. Preliminary diagrams to state " Preliminary, Not for Construction." Final Approved Site Plan to be PE Stamped. 4. System Summary Table inlcuding system ratings DC/AC, inverters, panels, quantities, etc. 5. Proper scale with North Arrow Bar. 6. Appropriate Turnaround provided. 7. Circuit name and ID provided at POI location. General Guidance: Main Disconnect Switch: C511 Customer Recloser: EASTERN & WESTERN DIVISION- CR512 / Customer Fuse: CJ512 CENTRAL DIVISION- R516/ Customer Fuse: J518 Customer Additional Disconnect Switch: C513 Customer Pole Numbers: EASTERN DIVISION/CENTRAL DIVISION - C(POI Pole)-1, C(POI Pole)-2, etc. WESTERN DIVISION: C-1, C-2, C-3, etc. ESB 751 Section 5.0 ESB 756B Section 5.1.1.3 | Open |  |  | Site Plan
Three-Line Diagram | Preliminary diagrams to state " Preliminary, Not for Construction." Final Utiltiy accepted diagrams to state "For Construction" and be PE Stamped Locations of Company Equipment shall be noted as "Utility Equipment is for information purposes only, is not for construction, and may be changed by the Utiltiy at any time in the future." General Guidance: Main Disconnect Switch: C511 Customer Recloser: EASTERN & WESTERN DIVISION- CR512 / Customer Fuse: CJ512 CENTRAL DIVISION- R516/ Customer Fuse: J518 Customer Additional Disconnect Switch: C513 Customer Pole Numbers: EASTERN DIVISION/CENTRAL DIVISION - C(POI Pole)-1, C(POI Pole)-2, etc. WESTERN : C-1, C-2, C-3, etc. ESB 751 Section 5.0 ESB 756 Section 5.1.1.6 | Open |  |  | Line Diagram
Three-Line Diagram | The three-line diagram to include all protective devices including ratings and classes in sufficient detail to show intended operation; all instrument transformers with ratios; power and station service transformers with ratios, kVA, winding configurations, impedances; etc. Circuit name and ID provided at POI location. Switches and/or fuses shall be shown as dead-ended on the source side of the equipment. Three-line diagram to show MV transformer and/or grounding transformer as-built values, post construction, prior to witness testing. ESB 751 Section 5.0 | Open |  |  | Line Diagram
Single-Line Diagram | The single-line diagram shall include all equipment shown on the three-line diagram as well as all requirements of the three-line diagram. The single-line and three-line must be consistent. Final Utility approved Single Line to be PE Stamped. | Open |  |  | Line Diagram
AC/DC Schematic | The electrical AC/DC control schematic to show all control diagrams of the equipment associated with the interconnection protective system and logic used to control the interconnection protective devices. Logic diagrams shall be provided for utility-grade relay functions meeting utility requirements (i.e. including grounding bank shunt trip or UVR schemes). ESB 756B Section 2.2.2.1.4 | Open |  |  | AC/DC Schematic
Profile Drawings | 1. Preliminary diagrams to state " Preliminary, Not for Construction." Final Utility accepted diagrams to state "For Construction" and be PE Stamped 2. The profile drawings shall consist of a minimum of two perpendicular cuts of the site plan. 3. A single drawing of the entire line-up shall be provided. These pole drawings shall match the equipment configuration of the line diagrams. Appropriate Clearances: 1. The Profile drawings shall demonstrate all approprate clearances phase-to-phase clearances, phase-to-ground clearances, and pole-to-pole distances. A clearance table shall be deemed sufficient for determing critical dimensions. ESB 753 Errata (May 2023) ESB 751 Section 5.0 ESB 753 Sections 4, 5, 6 | Open |  |  | Pole/Switchgear Profile Drawings
Profile Drawings | Labeling Requirements: Main Disconnect Switch: C511 Customer Recloser: EASTERN & WESTERN DIVISION- CR512 / Customer Fuse: CJ512 CENTRAL DIVISION- R516/ Customer Fuse: J518 Customer Additional Disconnect Switch: C513 Customer Pole Numbers: EASTERN DIVISION/CENTRAL DIVISION - C(POI Pole)-1, C(POI Pole)-2, etc. WESTERN DIVISION: C-1, C-2, C-3, etc. ESB 753 Errata (May 2023) ESB 753 Sections 4, 5, 6 ESB 756 section 7.2.1 | Open |  |  | Pole/Switchgear Profile Drawings
Profile Drawings | Pole Requirements: 1. Poles shall be minimum Class 3, full-length penta treatment, conforming to the standards of EEI TD-103 and ANSI O5.1. Alternate pole treatments subject ot acceptance by the utiltiy where applicable. 2. Poles shall be a minimum of 40' in height, set at a minimum depth of 6'. but shall require additional depth for poles greater than 40' in height, minimum 10% of height + 2'. 3. The crossarm shall measure 3½" x 4½" x 8' minimum, conforming to specifications of EEI TD-90. A dead-end crossarm, such as a riser pole, must be a double-crossarm if made of wood. ESB 753 Errata (May 2023) ESB 753 Sections 4, 5, 6 | Open |  |  | Pole/Switchgear Profile Drawings
Profile Drawings | Structure Guying: 1. Service Entrance Guy wires shall be 25' minimum lead with insulating rod. The section of the guy wire closest to the insulating rod shall be bonded to neutral. 2. Service Entrance Guy wires shall utilize an insulating rod that is minimum of 54" long, or longer, if there is the potential to come into contact with energized equipment upon failure of the guy wire anchor. 3. Service Entrance primary conductor clearance to the insulating rod shall be a minimum of 6" for down guys or a minimum of 11" for span guys. 4. Serice Entrance Guy Anchor shall be buried a minimum of 6' in the ground and shown in sufficient detail in drawing. Minimum 200 sq inch expanding type required anchor or equivalent anchor. 5. The Customer's overhead conductors shall have a minimum clearance of 22' from final grade at midspan 6. Minimum distance between primary and neutral shall be 72". ESB 753 Errata (May 2023) ESB 753 Sections 4, 5, 6 | Open |  |  | Pole/Switchgear Profile Drawings
Profile Drawings | Service Entrance Switch (GOAB) 1. The switch shall be mounted so that the handle will be a minimum of 3'6" above grade. 2. The main disconnect switch mechanism shall be connected to the grounding grid near the operating handle by means of a flexible, tinned copper braid of at least 200 Ampere rating. The grounding grid and the switch handle's ground strap shall be connected to the pole's grounding conductor. 3. The disconnect switch shall be installed to have the line connection (jaw side) of the switch connected to the utility source. The hinge side of switch shall be connected electrically towards the customer DER. 4. All non-current-carrying metallic parts shall be bonded to the equipment ground with a stranded #4 AWG bare copper conductor. This includes switch frame (unless composite), guy wires, switch base, and the neutral conductor to the ground grid. 5. A separate down ground shall be installed for surge arresters (#4 AWG). It is recommended that the equipment and arrester grounds be installed on opposite sides of the pole where applicable. 6. Down grounds and ground rods shall be installed in accordance with ESB 753 Figure 5. 7. Potential Equalizing Grid Shall be designed and installed to ensure ground contact is met at all times during equipment handling/operation. 8. A copperweld mesh shall be installed below the operating handle of the switch, recloser cabinet, and meter cluster to protect servicing personnel. It is recommended that the Customer installs a grounding grid below any of their additional equipment that has the potential to become energized. This shall be installed in accordance with ESB 753 Figure 5. A separate customer provided diagram of the potential equalizing grid will be considered sufficient in determining acceptance of the proposed installation. 9. Full ground loop to be installed around the PCC equipment and connected to each ground mesh at all poles or each grounding conductor. (Delta installations only) This ground loop shall have a minimum depth of 18" below grade. ESB 753 Errata (May 2023) ESB 753 Sections 4, 5, 6, 7.4 ESB 753 Figure 5 | Open |  |  | Pole/Switchgear Profile Drawings
Profile Drawings | Service Protection 1. The service protection shall be physically and electrically connected in accordance with ESB 753 and ESB 756. relay test switches installed such that the switch blades open away form the relay. 2. Where the Customer utilizes a recloser or relay device for main protection, the control power may be installed on the utiltiy side of the protective device. Control power transformers connected ahead of utility metering shall solely be used to serve the control circuit for the main protective device. auxillary load shall be connected on the load side of the primary metering transformers. 3. All non-current-carrying metallic parts shall be bonded to the equipment ground with a minimum stranded #4 AWG copper conductor. This includes switch frame (unless composite), guy wires, switch base, and the neutral conductor. 4. A separate down ground shall be installed for surge arresters (#4 AWG). It is recommended that the equipment and arrester grounds be installed on opposite sides of the pole where applicable. 5. Down grounds and ground rods shall be installed in accordance with ESB 753 Figure 5. 6. Where installing a recloser ,A copperweld mesh shall be installed below the recloser cabinet to protect servicing personnel. It is recommended that the Customer installs a equipotential mat below any of their additional equipment that has the potential to become energized. This shall be installed in accordance with ESB 753 Figure 5. A separate customer provided diagram of the potential equalizing grid will be considered sufficient in determining acceptance of the proposed installation. Potential Equalizing Grid shall be designed and installed to ensure ground contact is met at all times during equipment handling/operation. 7. Full ground loop to be installed around the PCC equipment and connected to each ground mesh at all poles or each grounding conductor. (Delta installations only) This ground loop shall have a minimum depth of 18" below grade. ESB 753 Errata (May 2023) ESB 753 Sections 4, 5, 6 ESB 753 Figure 5
Profile Drawings | Utility Metering on Customer Pole: 1. Minimum distance between bottom of PT/CT mount shall be 20" to the system neutral. 2. The CT polarity mark shall go towards the utility source. 3. Meter shall have 1½" rigid metallic or schedule 80 P.V.C. conduit installed by Customer. 4. Meter socket enclosure height between 4' and 5'6". 5. All non-current-carrying metallic parts shall be bonded to the equipment ground with a stranded #4 AWG copper conductor. This includes meter socket enclosure, guy wires, switch base, and the neutral conductor to the equipotential mat. 6. A separate down ground shall be installed for surge arresters (#4 AWG). It is recommended that the equipment and arrester grounds be installed on opposite sides of the pole where applicable. 7. Down grounds and ground rods shall be installed in accordance with ESB 753 Figure 5. 8.) A copperweld mesh shall be installed below the operating handle of the switch, recloser cabinet, and meter cluster to protect servicing personnel. It is recommended that the Customer installs a equipotential mat below any of their additional equipment that has the potential to become energized. This shall be installed in accordance with ESB 753 Figure 5. A separate customer provided diagram of the potential equalizing grid will be considered sufficient in determining acceptance of the proposed installation. Potential Equalizing Grid Shall be designed and installed to ensure ground contact is met at all times during equipment handling/operation. 9.) Full ground loop to be installed around the PCC equipment and connected to each ground mesh at all poles or each grounding conductor. (Delta installations only) This ground loop shall have a minimum depth of 18" below grade. ESB 753 Errata (May 2023) ESB 753 Sections 4, 5, 6 ESB 753 Figure 5 | Open |  |  | Pole/Switchgear Profile Drawings
Switchgear and Underground Service Shop Drawing(s) | Location and labeling on shop drawing of all field devices including switchgear bay labels and/or modular units. Preliminary diagrams to state " Preliminary, Not for Construction." Final Utility accepted diagrams to state "For Construction" and be PE Stamped General Guidance: Main Disconnect Switch: C511 Customer Recloser: EASTERN & WESTERN DIVISION- CR512 / Customer Fuse: CJ512 CENTRAL DIVISION- R516/ Customer Fuse: J518 Customer Additional Disconnect Switch: C513 Customer Pole Numbers: EASTERN DIVISION/CENTRAL DIVISION - C(POI Pole)-1, C(POI Pole)-2, etc. WESTERN DIVISION: C-1, C-2, C-3, etc - Switchgear bay number or cabinet labeling ESB 751 Section 5.0 ESB 756B Sections 5.1.1.3, 7.4.7 EBS 758 Section L.30 | Open |  |  | Pole/Switchgear Profile Drawings
Switchgear and Underground Service Shop Drawing(s) | The profile drawings shall consist of a side profile of the switchgear. Profiles shall be in sufficient detail to allow for the Company's determination of electrical and working space clearances. A single drawing of the entire lineup shall be provided. This lineup shall include Customer conduit trench from Utility Riser Pole to the main disconnect cabinet including all applicable clearances per ESB 758. Shall the Customer propose modular/separate units, profile drawings shall be required for each unit to be installed. ESB 752 Figure 3 ESB 758 Figure 1 ESB 758 Errata (July 2020) ESB 759B Section 28.0 | Open |  |  | Pole/Switchgear Profile Drawings
Switchgear and Underground Service Shop Drawing(s) | Main Disconnect (GOAB) Cubicle - Customer shall provide an adequate viewing window for the main generator disconnect switch - Customer shall provide dual padlock provisions for 24/7 Company access - Customer to install an accessible lug on the line side of each phase of the main switch for grounding or testing - Customer to provide viewing window for their additional C513 disconnect. - Minimum 36" vertical clearance from top of conduit to base of bus attachment (anything greater requires a cable grip) - Minimum 10' clearance to be made for incoming cable compartment. (Usually backside of Main Disconnect compartment) - Receiving bus to be drilled to receive 2-hole NEMA pad - Minimum BIL rating of 95 kV BIL for receiving equipment - 72" cubicle height typical - 36"-48" cubicle width typical - 48" cubicle depth typical - Customer to show phase edge to phase edge spacing of buswork ESB 752 Figure 3 ESB 758 Section L ESB 758 Figure 2 ESB 758 Errata (July 2020) ESB 756B Section 5.0
Switchgear and Underground Service Shop Drawing(s) | Primary cable and conduit with clearances shown including applicable handholes. - Customer to furnish, install, and own the primary conduit from the Company's pole to the service entrance equipment - Conduit to be at least 4" in diameter and slope 2" per 100' toward a handhole (if applicable) for drainage - Recommended spare conduit be installed - Conduit to be buried a minimum of 30" below grade unless otherwise specified by the Company - Customer to include note to install pull wire in each conduit - Riser shall consist of 36" minimum radius with a 90 degree bend and 10' vertical length of RGS conduit - Riser grounded via ground clamp on top of conduit minimum 8' high and 6" from top of conduit Handholes for underground conduit and cable provided based on appropriate cable length and conduit installation. Location of handholes (if applicable) to be specified on site plan as well. ESB 758 Sections H.21, H.22 ESB 758 Section H ESB 759 section 28 | Open |  |  | Pole/Switchgear Profile Drawings
Switchgear and Underground Service Shop Drawing(s) | Metering Cubicle: - Minimum 72" cubicle height typical - Minimum 48" cubicle depth typical - Minimum 36" wide for Company Metering Cubicle solely used for billing meter transformers. - Customer to show phase edge to phase edge spacing of buswork - For outdoor meter cabinets, refer to ESB 750 section 7.4 -Customer to install a means for grounding each phase on the line and load side the metering transformers. - Customer to provide space and supports for metering transformers as specified by the Company. - Minimum 10' clearance to be made in front of meter compartment - Customer to install and furnish conduit from metering transformers to billing meter panel exclusively for metering transformer cables - Conduit shall be a minimum of 1½" diameter steel or equivalent approved conduit - Conduit should be installed using the shortest practical distance no greater than 100' with a maximum of two (2) 90-degree bends - No instrument transformers to be installed closer than 6" to the ground floor of the compartment - Heating of metering cubicle required minimum 250 Watt, thermostatically controlled also containing a 120/240 VAC duplex receptacle ESB 750 Sections 7.1.2.2, 7.3 ESB 758 Errata (July 2020) ESB 758 Section M ESB 752 Figure 3 ESB 758 Section L ESB 758 Figure 2 ESB 758 Errata (July 2020) | Open |  |  | Pole/Switchgear Profile Drawings
Switchgear and Underground Service Shop Drawing(s) | Meter Socket Enclosure: - Meter socket enclosure Height 3½' to 5½' above grade to center of meter - Minimum of 4' clearance in front of meter socket for working space - Minimum headroom of 84" - Minimum 30" working space on side of meter can - Standalone meter cabinet installations shall follow ESB 750 Section 7.1.2.2 and ESB 750 Section 7.7.3 ESB 750 Sections 7.1.2.2, 7.7.3 | Open |  |  | Pole/Switchgear Profile Drawings
Switchgear and Underground Service Shop Drawing(s) | Grounding: - Appropriate ground grid to be installed consisting of bare #4/0 AWG CU conductor - Outer loop pattern buried 6" in depth around the switchgear pad - Minimum of two (2) driven ground rods to achieve maximum ground resistance of 10 Ohms - Minimum of two (2) grounding connections from ground grid to switchgear ground bus shown - Metallic conduit to be grounded to ground grid via #4/0 CU - Surge arresters mounted on load side of main switch with rating per installation (8.4 MCOV 10 kV) - A ⅝" diameter, 24" long CU ground bail connected to ground bus at both ends 7" behind door and 5" above door sill ESB 758 Errata (July 2020) ESB 758 Sections J, L | Open |  |  | Pole/Switchgear Profile Drawings
Switchgear and Underground Service Shop Drawing(s) | Bollarding: - Bollards required where equipment is close in proximity to vehicular traffic or access road subject to snow removal - 10' minimum clearance to be maintained from swtichgear to nearby structures/equipment for maintenance and operation. - Number and location of bollards determined by Company - Bollards supported with 12" minimum diameter steel with concrete footing 6" below grade - Bollards 5' above ground and 4' below ground - Bollards shall not impede door opening of 100 degrees - 5 ft typical spacing between bollards - 3ft minumum clearance from front of switchgear to bollards ESB 759B Sections 8, 9, 10, 29 | Open |  |  | Pole/Switchgear Profile Drawings
Datasheet - Transformer | Manufacturer datasheet (must include kVA, %Z, X/R, winding, voltage) ESB 751 Section 5.0 | Open |  |  | Tech Sheets
Datasheet - Ground Bank NGR | Manufacturer datasheet (must include kVA, %Z, X/R, winding, voltage, Ohmic impedance (Ohms/phase) ESB 751 Section 5.0 | Open |  |  | Tech Sheets
Datasheet - Disconnect Switch | Manufacturer datasheet (must include nameplate, rating, ½" ice break capability, mounting, tension, BIL, etc) - For switchgear applications, specific ratings and electrical characteristics to be provided via a datasheet. ESB 751 Section 5.0 ESB 756 section 7.4 | Open |  |  | Tech Sheets
Datasheet - Surge Arrester | Manufacturer datasheet (8.4 MCOV 10 kV on 13.2 kV Wye-Grounded EPS) NOTE: Lighting Arrester Ratings shall be sized in accordance with the applicable primary service voltage. Customer shall coordinate with National Grid where interconnection voltage is not 13.2 kV Wye-Grounded. ESB 753 Section V D.2 | Open |  |  | Tech Sheets
Datasheet - Inverter | Manufacturer datasheet (including UL 1741 SB certification to IEEE 1547 2018 standards) Factory derating letter, if necessary. ESB 751 Section 5.0 ESB 756 | Open |  |  | Tech Sheets
Datasheet - Relay / Recloser Fuse | Manufacturer datasheet for Customer main protective device showing full BOM or catalog number, appropriate ratings, and electrical characteristics. | Open |  |  | Tech Sheets
Protection Settings | Customer to provide table/list of protection settings for the inverters &/or main protective device including all instrument transformer ratios, pickups(sec,pri), Curve selection. Etc. Protection settings shall be submitted in table format on dedicated drawing/company title block. | Open |  |  | Tech Sheets
Datasheet - Generator | Manufacturer datasheet (if not inverter based) ESB 751 Section 5.0 ESB 756 | Open |  |  | Tech Sheets
***STORMS 431R Requirement SHALL NOT BE PARTIALED/COMPLETED if any of the above line items are Open*** ***STORMS 431R Requirement SHALL NOT BE PARTIALED/COMPLETED if any of the above line items are Open*** ***STORMS 431R Requirement SHALL NOT BE PARTIALED/COMPLETED if any of the above line items are Open*** ***STORMS 431R Requirement SHALL NOT BE PARTIALED/COMPLETED if any of the above line items are Open*** ***STORMS 431R Requirement SHALL NOT BE PARTIALED/COMPLETED if any of the above line items are Open*** ***STORMS 431R Requirement SHALL NOT BE PARTIALED/COMPLETED if any of the above line items are Open***
Test Report - Transformer | As-built manufacturer test report of specific transformer utilized for the project (must include kVA, %Z, X/R, winding, voltage) | Open |  |  | Test Reports
Test Report - Ground Bank | As-built manufacturer test report of specific ground bank utilized for the project (must include kVA, %Z, X/R, winding, voltage) | Open |  |  | Test Reports
Protective Device Settings | Relay settings file provided (acSELerator .rdb file or equivalent) Time Current Curves (TCC) for fusing, including datasheet ESB 751 Section 5.0 | Open |  |  | Relay(RDB) / Fuse (TCC)
Electrical Inspection by Code Enforcement Authority | The Customer shall provide evidence of an electrical inspection, performed by the Authority Having Jurisdiction or their assigned agent. The Customer's third party or municipal electrical inspection approval certificate shall be submitted to the Company prior to the Company's on-site field audit of the Customer's site. The 625R requirement shall be completed in STORMS. | Open |  |  | Closeout Documentation
Customer Notification of Satisfactory Completion of Construction | At least two weeks prior to the Company's field audit, the Customer shall provide written documentation of satisfactory construction completion. This shall include the contractor's functional testing schedule and Testing and Commissioning Report for the protective relay systems. Customer to supply Applied settings File in EPRII Common File Format where applicable. ESB 751 Section 6.0 | Open |  |  | Closeout Documentation
Photo Documentation | Prior to scheduling Facility Audit, the Customer shall submit to National Grid photos of the following: 1. Equipotential mat and below grade grounding installation. 2. Placards on all equipment where required. See National Grid Labeling requirements. ESB 756B Section 7.2.1 ESB 753 Figure 5 | Open |  |  | Construction Photos
As-Built Documentation | As-build documentation is required at the end of the design process. The Customer shall submit a full set of the drawings and documents in States B and C of ESB 751. | Open |  |  | As-Built Documentation
***Company Field Audit SHALL NOT BE SCHEDULED if any of the above line items are Open*** ***Company Field Audit SHALL NOT BE SCHEDULED if any of the above line items are Open*** ***Company Field Audit SHALL NOT BE SCHEDULED if any of the above line items are Open*** ***Company Field Audit SHALL NOT BE SCHEDULED if any of the above line items are Open*** ***Company Field Audit SHALL NOT BE SCHEDULED if any of the above line items are Open*** ***Company Field Audit SHALL NOT BE SCHEDULED if any of the above line items are Open***
***STORMS 609R Requirement SHALL NOT BE COMPLETED if any of the above line items are Open*** ***STORMS 609R Requirement SHALL NOT BE COMPLETED if any of the above line items are Open*** ***STORMS 609R Requirement SHALL NOT BE COMPLETED if any of the above line items are Open*** ***STORMS 609R Requirement SHALL NOT BE COMPLETED if any of the above line items are Open*** ***STORMS 609R Requirement SHALL NOT BE COMPLETED if any of the above line items are Open*** ***STORMS 609R Requirement SHALL NOT BE COMPLETED if any of the above line items are Open***
Maintenance Plan | The maintenance plan shall identify the specific equipment to be maintained and a maintenance schedule. See the Company's ESB 755 for guidance. Where site specific conditions including but not limited to Utility access, require site specific/equipment maintenance, the customer shall include all maintenance activities and associated intervals within the maintenance plan. | Open |  |  | Witness Testing
Energization Plan | The Customer shall designate an energization coordinator and prepare and submit an energization plan to the Company for review and comment. The energization plan shall include but not be limited to such items as: - Switching control procedures; - Required phasing and synchronization tests; - Load and operational tests required to place the apparatus or systems online without risk to the electrical infrastructure; and - Sequence of operations The sequence of operations explains how automated switching will occur based on planned and unplanned outage events, and the automatic restoration back to original conditions. Correct breaker, bus, transformer, and disconnect nomenclature shall be referenced throughout this procedure, and shall be consistent with the submitted three-line diagram. | Open |  |  | Witness Testing
Sequence of Operations | The Company requires a Sequence of operations (SOO) from the Customer. The Company also requires an operating description from the Customer for normal, alternate, and emergency (if proposed) operations, if the Customer desires to operate in these modes and in the event of any changes to the existing procedures. ESB 756B Section 9.0 | Open |  |  | Witness Testing
Witness Test (Testing and Commissioning Plan) | The testing and commissioning plan shall include the procedural steps for testing and functional verification of the Customer's relay, breakers, interlocking schemes, and related protection devices. The Company has an interest in witnessing portions of the overall test specific to those devices which interconnect to the Company's EPS. The Company reserves the right to modify the testing procedure as necessary to ensure the integrity of the Company's EPS. | Open |  |  | Witness Testing
***STORMS 649R Requirement SHALL NOT BE COMPLETED nor witness test scheduled if any of the above line items are Open*** ***STORMS 649R Requirement SHALL NOT BE COMPLETED nor witness test scheduled if any of the above line items are Open*** ***STORMS 649R Requirement SHALL NOT BE COMPLETED nor witness test scheduled if any of the above line items are Open*** ***STORMS 649R Requirement SHALL NOT BE COMPLETED nor witness test scheduled if any of the above line items are Open*** ***STORMS 649R Requirement SHALL NOT BE COMPLETED nor witness test scheduled if any of the above line items are Open*** ***STORMS 649R Requirement SHALL NOT BE COMPLETED nor witness test scheduled if any of the above line items are Open***

## Pre-Witness Test Checklist (hidden)
Requirement | Status
All necessary placarding has been completed (i.e. poles, equipment, etc.) | Open
National Grid meter has been installed. | Open
All test reports have been received. | Open
Photos of below grade grounding installation shall be submitted to National Grid for review prior to backfill. | Open
All Customer poles and interconnection devices, including switches, breakers, fuses, busses and transformers shall be uniformly placarded with permanently affixed metal or plastic labels. | Open
The main generator disconnect switch shall be capable of being locked in the open position and have provisions for both Company and Generator-Owner or IC padlocks. | Open
Should the disconnecting means be located behind the IC's locked gate, double locking is required, where both the Company's and IC's locks would be employed. | Open
The utility meter enclosure shall be labeled with the following: "WARNING: DUAL POWER SOURCES" The Customer meter enclosure shall be labeled with the folloing: " Customer-Owned Meter" | Open
The final approved single-line diagram shall be laminated and located on the customer site at the GOAB in a PVC pipe. | Open
The GOAB Shall have a permanent nameplaate at the switch pole indication " GOAB" or Main Generator Disconnect | Open
Customer fuse picture to be provided. | Open
Customer Notifcation of Satisfactory Completion of Construction | At least two weeks prior ot the Company's field audit, the Interconnection Customer shall provide written documentation of satisfactory construction completion. This shall include the contractor's functional testing schedule and Testing and Commissioning Plan for the protective relay systems.
Electrical Inspection by Code Enforcement Authority | The Customer shall provide evidence of an electrical inspection, performed by the Authority Having Jurisdiction or their assigned agent. The Customer's third party or minicipal electrical inspection approval certificate shall be submitted to the Company before the Company's on-site field audit of the Customer's site.
Company's Field Audit | The Company shall make a final walk-through field audit of the Customer site to confirm the construction is in substantial conformance with the Company accepted design submittals. The Company will also verify final grounding attachments, observe related safety signs and fencing, and ensure the Company has access to the main disconnect device, as a condition of acceptance. During the Company's Field Audit, the Company shall verify the permanently installed placards on the specific devices, as required by the Company. The placards shall be clearly visible to operators.
Customer Operating Agreement and Company Operating Diagram | National Grid requires a list of 24 hour emergency contacts from the Customer, once their facility is interconnected to the National Grid distribution system. The Customer shall provide a list of the primary and alternate contact personnel in the order in which National Grid should attempt to contact them. The Company will issue the Customer Operating Agreement and a Company Operating Diagram specific to the Customer installation, each containing the customer's emergency contacts.
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open
Open